## buses
bus_name | type | zone | vn_kv | min_vm_pu | max_vm_pu | in_service
Bus1 | b | Bus1 | 230 | 0.97 | 1.05 | 1
Bus2 | b | Bus2 | 230 | 0.97 | 1.05 | 1
Bus3 | b | Bus3 | 230 | 0.97 | 1.05 | 1
Bus4 | b | Bus4 | 230 | 0.97 | 1.05 | 1
Bus5 | b | Bus5 | 230 | 0.97 | 1.05 | 1
Bus6 | b | Bus6 | 230 | 0.97 | 1.05 | 1

## loads_sector_allocation
bus_no | load_mw | agriculture_percent | large_user_percent | residential_percent | government_percent | industrial_percent | commercial_percent | office_percent | customer_types
Bus2.8 | 20 | 0 | 0 | 50.95 | 22.2 | 12.95 | 13.9 | 0 | industrial,government,residential,commercial
Bus3.3 | 85 | 0 | 65.29 | 23.16 | 0 | 4.58 | 4.35 | 2.62 | large users,industrial,government,residential,commercial
Bus4.3 | 40 | 0 | 0 | 37.12 | 0 | 42.08 | 20.8 | 0 | industrial,residential,commercial
Bus5.1 | 20 | 0 | 0 | 50.05 | 33.3 | 0 | 9.25 | 7.4 | government,office,residential,commercial
Bus6.2 | 20 | 37 | 0 | 40.8 | 0 | 12.95 | 9.25 | 0 | industrial,agriculture,residential,commercial

## lines
line_no | from_bus | to_bus | length_km | type
L1 | Bus1.5 | Bus3.4 | 75 | ol
L2 | Bus2.2 | Bus4.2 | 250 | ol
L3 | Bus1.7 | Bus2.4 | 200 | ol
L4 | Bus3.5 | Bus4.5 | 50 | ol
L5 | Bus3.1 | Bus5.2 | 50 | ol
L6 | Bus1.2 | Bus3.2 | 75 | ol
L7 | Bus2.6 | Bus4.4 | 250 | ol
L8 | Bus4.1 | Bus5.4 | 50 | ol
L9 | Bus5.3 | Bus6.1 | 50 | ol

## switches
sw_name | element | to_bus | type | et | closed
G1 DS1.1 | Bus1.G1 | Bus1.1 | DS | b | 1
L6 DS1.2 | L6 | Bus1.2 | LBS | l | 1
L1 DS1.3 | L1 | Bus1.5 | LBS | l | 1
L3 DS1.4 | L3 | Bus1.7 | LBS | l | 1
CB1.1 | Bus1.1 | Bus1.2 | CB | b | 1
CB1.2 | Bus1.2 | Bus1.3 | CB | b | 1
CB1.3 | Bus1.3 | Bus1.4 | CB | b | 1
CB1.4 | Bus1.4 | Bus1.5 | CB | b | 1
CB1.5 | Bus1.5 | Bus1.6 | CB | b | 1
CB1.6 | Bus1.6 | Bus1.7 | CB | b | 1
CB1.7 | Bus1.7 | Bus1.1 | CB | b | 1
G5 DS2.1 | Bus2.G5 | Bus2.2 | DS | b | 1
G8-9 DS2.2 | Bus2.G8-9 | Bus2.3 | DS | b | 1
L3 DS2.3 | L3 | Bus2.4 | LBS | l | 1
G7 DS2.4 | Bus2.G7 | Bus2.5 | DS | b | 1
L7 DS2.5 | L7 | Bus2.6 | LBS | l | 1
G10-11 DS2.6 | Bus2.G10-11 | Bus2.7 | DS | b | 1
G6 DS2.9 | Bus2.G6 | Bus2.8 | DS | b | 1
CB2.1 | Bus2.1 | Bus2.2 | CB | b | 1
CB2.2 | Bus2.2 | Bus2.3 | CB | b | 1
CB2.3 | Bus2.3 | Bus2.4 | CB | b | 1
CB2.4 | Bus2.4 | Bus2.5 | CB | b | 1
CB2.5 | Bus2.5 | Bus2.6 | CB | b | 1
CB2.6 | Bus2.6 | Bus2.7 | CB | b | 1
CB2.7 | Bus2.7 | Bus2.8 | CB | b | 1
CB2.8 | Bus2.8 | Bus2.9 | CB | b | 1
CB2.9 | Bus2.9 | Bus2.1 | CB | b | 1
L6 DS3.1 | L6 | Bus3.2 | LBS | l | 1
L1 DS3.4 | L1 | Bus3.4 | LBS | l | 1
L4 DS3.5 | L4 | Bus3.5 | LBS | l | 1
L5 DS3.6 | L5 | Bus3.1 | LBS | l | 1
CB3.1 | Bus3.1 | Bus3.2 | CB | b | 1
CB3.2 | Bus3.2 | Bus3.3 | CB | b | 1
CB3.3 | Bus3.3 | Bus3.4 | CB | b | 1
CB3.4 | Bus3.4 | Bus3.5 | CB | b | 1
CB3.5 | Bus3.5 | Bus3.1 | CB | b | 1
L4 DS4.1 | L4 | Bus4.5 | LBS | l | 1
L8 DS4.2 | L8 | Bus4.1 | LBS | l | 1
L2 DS4.3 | L2 | Bus4.2 | LBS | l | 1
L7 DS4.6 | L7 | Bus4.4 | LBS | l | 1
CB4.1 | Bus4.1 | Bus4.2 | CB | b | 1
CB4.2 | Bus4.2 | Bus4.3 | CB | b | 1
CB4.3 | Bus4.3 | Bus4.4 | CB | b | 1
CB4.4 | Bus4.4 | Bus4.5 | CB | b | 1
CB4.5 | Bus4.5 | Bus4.1 | CB | b | 1
L5 DS5.3 | L5 | Bus5.2 | LBS | l | 1
L9 DS5.4 | L9 | Bus5.3 | LBS | l | 1
L8 DS5.5 | L8 | Bus5.4 | LBS | l | 1
CB5.1 | Bus5.1 | Bus5.2 | CB | b | 1
CB5.2 | Bus5.2 | Bus5.3 | CB | b | 1
CB5.3 | Bus5.3 | Bus5.4 | CB | b | 1
CB5.4 | Bus5.4 | Bus5.1 | CB | b | 1
L9 DS6.1 | L9 | Bus6.1 | LBS | l | 1
CB6.1 | Bus6.1 | Bus6.2 | CB | b | 1
CB6.2 | Bus6.2 | Bus6.1 | CB | b | 1

## gens
gen_no | name | type | bus_no | unit_size_mw | slack
G1 | G1 40MW Thermal Plant DS | Thermal | Bus1.G1 | 40 | FALSE
G2 | G2 40MW Thermal | Thermal | Bus1.G2 | 40 | TRUE
G3 | G3 10MW Gas | Thermal – Gas | Bus1.G3 | 10 | FALSE
G4 | G4 20MW Thermal | Thermal | Bus1.G4 | 20 | FALSE
G5 | G5 5MW Hydro DS | Hydro | Bus2.G5 | 5 | FALSE
G6 | G6 5MW Hydro DS | Hydro | Bus2.G6 | 5 | FALSE
G7 | G7 40MW Hydro DS | Hydro | Bus2.G7 | 40 | FALSE
G8 | G8 20MW Hydro DS Coupled(G9) | Hydro | Bus2.G8-9 | 20 | FALSE
G9 | G9 20MW Hydro DS Coupled(G8) | Hydro | Bus2.G8-9 | 20 | FALSE
G10 | G10 20MW Hydro DS Coupled(G11) | Hydro | Bus2.G10-11 | 20 | FALSE
G11 | G11 20MW Hydro DS Coupled(G10) | Hydro | Bus2.G10-11 | 20 | FALSE

## lines_reliability
line_no | permanent_outage_rate_occ_per_year | permanent_outage_duration_hr | momentary_outage_rate_occ_per_year
L1 | 1.5 | 10 | 3.75
L2 | 5 | 10 | 12.5
L3 | 4 | 10 | 10
L4 | 1 | 10 | 2.5
L5 | 1 | 10 | 2.5
L6 | 1.5 | 10 | 3.75
L7 | 5 | 10 | 12.5
L8 | 1 | 10 | 2.5
L9 | 1 | 10 | 2.5

## lines_impedance_current_rating
line_no | r_ohm_pu | x_ohm_pu | B_2_pu | current_rating_pu
L1 | 0.0342 | 0.18 | 0.0106 | 0.85
L2 | 0.114 | 0.6 | 0.0352 | 0.71
L3 | 0.0912 | 0.48 | 0.0282 | 0.71
L4 | 0.0228 | 0.12 | 0.0071 | 0.71
L5 | 0.0028 | 0.12 | 0.0071 | 0.71
L6 | 0.0342 | 0.18 | 0.0106 | 0.85
L7 | 0.114 | 0.6 | 0.0352 | 0.71
L8 | 0.0228 | 0.12 | 0.0071 | 0.71
L9 | 0.0028 | 0.12 | 0.0071 | 0.71

## line_bus_common_mode_circuit_reliability
line_pair | from_bus | to_bus | line_no | common_length_km | outage_rate_occ_per_year | outage_duration_hr
A | Bus1 | Bus3 | L1 | 75 | 0.15 | 16
A | Bus1 | Bus3 | L6 | 75 | 0.15 | 16
B | Bus2 | Bus4 | L2 | 250 | 0.5 | 16
B | Bus2 | Bus4 | L7 | 250 | 0.5 | 16
Common Mode Data for the Circuits on a Common Right-of-Way or a Common Tower

## gen_reliability
gen_no | unit_size_mw | type | num_units | forced_outage_rate | failure_rate_lambda_per_yr | repair_rate_mu_per_year | scheduled_maintenance_weeks_per_year
G5,G6 | 5 | Hydro | 2 | 0.01 | 2 | 198 | 2
G3 | 10 | Thermal | 1 | 0.02 | 4 | 196 | 2
G8,G9,G10,G11 | 20 | Hydro | 4 | 0.015 | 2.4 | 157.6 | 2
G4 | 20 | Thermal | 1 | 0.025 | 5 | 195 | 2
G7 | 40 | Hydro | 1 | 0.02 | 3 | 147 | 2
G1,G2 | 40 | Thermal | 2 | 0.03 | 6 | 194 | 2

## gen_cost
gen_no1 | gen_no2 | unit_size_mw | type | num_units | loading_order_1 | loading_order_2 | var_cost_fuel_doll_per_mwh | var_cost_operating_doll_per_mwh | total_var_cost | fixed_cost_k_doll_per_yr | capital_cost_M_doll
G7 |  | 40 | Hydro | 1 | 1 | 1 | 0.45 | 0.05 | 0.5 | 100 | 160
G8 | G9 | 20 | Hydro | 2 | 2,3 | 2,3 | 0.45 | 0.05 | 0.5 | 50 | 80
G1 | G2 | 40 | Thermal | 2 | 8,9 | 4,5 | 9.5 | 2.5 | 12 | 790 | 80
G4 |  | 20 | Thermal | 1 | 10 | 6 | 9.75 | 2.5 | 12.25 | 680 | 60
G3 |  | 10 | Thermal | 1 | 11 | 7 | 10 | 2.5 | 12.5 | 600 | 40
G10 | G11 | 20 | Hydro | 2 | 4,5 | 8,9 | 0.45 | 0.05 | 0.5 | 50 | 80
G5 | G6 | 5 | Hydro | 2 | 6,7 | 10,11 | 0.45 | 0.05 | 0.5 | 12.5 | 40

## gen_gas_cost_reliability
unit_size_mw | type | FOR | MTTF_hr | MTBR_hr | var_cost_fuel_doll_per_mwh | var_cost_operating_doll_per_mwh | fixed_cost_k_doll_per_yr | capital_cost_M_doll
10 | Gas | 0.12 | 550 | 75 | 52 | 4.5 | 40 | 5

## gen_unit_mvar_capacities
unit_size_mw | mvar_minimum | mvar_maximum
5 | 0 | 5
10 | 0 | 7
20 | -7 | 12
40 | -15 | 17

## equipment_reliability_data
type | active_failure_rate_fail_per_hr | passive_failure_rate_fail_per_hr | avg_outage_duration_hr | maintenance_outage_rate_occ_per_year | maintenance_duration_hr | switching_time_hr
Circuit Breaker | 0.0066 | 0.0005 | 72 | 0.2 | 108 | 1
Bus Section | 0.22 |  | 10
Station Transformer | 0.02 |  | 768 | 0.2 | 72 | 1

## trafos
name | from_bus | to_bus | std_type | parallel | in_service
G1 T1.1
G2 T1.2
G3 T1.3
G4 T1.4
G5 T2.1
G6 T2.2
G7 T2.3
G8 T2.4
G9 T2.5
G10 T2.6
G11 T2.7